## PTC
| 천 세 산 업 주 식 회 사 CHEON SEI IND. CO., LTD. | [5 empty] | METERING PUMP
DATA SHEET
1 | PURCHASER | [5 empty] | ITEM NO.
2 | PROJECT | [5 empty] | SERVICE
3 | JOB NO. | [5 empty] | QUANTITY |  |  |  | SET
4 | OPERATION CONDITIONS | [5 empty] | PUMP SPECIFICATION
5 | LIQUID NAME | [5 empty] | MODEL |  |  | KHV1-12S-PTC-FS
6 | PUMPING TEMP. |  |  |  |  | ℃ | PUMPING TEMP. |  |  | AMB
7 | VISCOSITY |  |  |  |  | CP | DIS. CAPACITY |  |  |  | MAX. |  | 100 | ㎖/min
8 | SPECIFIC GR. | [5 empty] | DIS. PRESS |  |  |  | MAX. |  | 10 | kgf/㎠
9 | CAPACITY |  |  |  |  | ㎖/min | RELIEF V/V SET. PRESS. | [5 empty] | 13 | kgf/㎠
10 | DIS. PRESS |  |  |  |  | kgf/㎠G | STROKE SPEED | [5 empty] | 116 | S.P.M
11 | SUC. PRESS |  |  |  |  | kgf/㎠G | PISTON DIAMETER | [5 empty] | 12 | mm
12 | NPSHa |  |  |  |  | M | STROKE LENGTH | [5 empty] | 10 | mm
13 | INSTALLATION | [5 empty] | NPSHr | [5 empty] | 2 | M
14 | CONSTRUCTION | [5 empty] | INSTALLATION |  |  | INDOOR
15 | DIAPHRAGM TYPE | HYDRAULIC |  |  |  |  | LIQUID END MATERIAL
16 | HEAD NUMBER | SINGLE |  |  |  |  | PUMP HEAD |  |  | PVC
17 | RELIEF VALVE | INTERNAL |  |  |  |  | DIAPHRAGM |  |  | PTFE + PFA
18 | MOTOR MOUNT | VERTICAL |  |  |  |  | CHECK BALL |  |  | CERAMIC
19 | CONNECTION TYPE | FLANGE |  |  |  |  | BALL GUIDE |  |  | GFPP
20 | SUC. SIZE | KS 10K 15A RF / LAP JOINT |  |  |  |  | BALL SEAT |  |  | SANTOPRENE
21 | DIS. SIZE | KS 10K 15A RF / LAP JOINT |  |  |  |  | JOINT |  |  | PVC
22 | CAPACITY CONTROL | [5 empty] | O-RING |  |  | SANTOPRENE
23 | TYPE | MANUAL |  |  |  |  | AC INDUCTION MOTOR SPEC.
24 | METHOD | STROKE ADJUSTMENT |  |  |  |  | MAKER |  |  | SHINKANG ELEC.
25 | FLOW RANGE | 10 TO 100% RATED |  |  |  |  | ENCLOSURE |  |  | TEFC
26 | PAINTING COLOR (Munsell No.) | [5 empty] | RATED OUTPUT |  |  | 0.2
27 | GEAR BOX, BED | 0.6PB 4.8/10.6 |  |  |  |  | VOLTAGE/PHASE/CYCLE |  |  | 220,380V / 3Φ/ 60HZ
28 | MOTOR | 0.6PB 4.8/10.6 |  |  |  |  | POLE / SPEED |  |  | 4P / 1700RPM
29 | [6 empty] | INSULATION CLASS |  |  | B
30 | APPROX. WEIGHT |  | 17.5 | KG |  |  | PROTECTION DEGREE |  |  | IP44
31 | [6 empty] | HUB SIZE |  |  | 21
32 | ACCESSORIES | [5 empty] | SPARE PARTS
33 | NAME | SPEC. |  |  |  | Q'TY | NAME |  |  | SPEC. |  |  |  | Q'TY
34
35
36
37
38 | REMARKS : | [5 empty] | REV. | PREPD BY | CHKD BY |  |  |  | APPRVD BY
39 | [6 empty] | 0 | H. R. CHA
41
| 양식 S-01-01 |  |  |  | CHEON SEI IND. CO., LTD. | [6 empty] | A4 (210×297)
| 천 세 산 업 주 식 회 사 CHEON SEI IND. CO., LTD. | [5 empty] | METERING PUMP
DATA SHEET
1 | PURCHASER | [5 empty] | ITEM NO.
2 | PROJECT | [5 empty] | SERVICE
3 | JOB NO. | [5 empty] | QUANTITY |  |  |  | SET
4 | OPERATION CONDITIONS | [5 empty] | PUMP SPECIFICATION
5 | LIQUID NAME | [5 empty] | MODEL |  |  | KHH1-12S-PTC-FS
6 | PUMPING TEMP. |  |  |  |  | ℃ | PUMPING TEMP. |  |  | AMB
7 | VISCOSITY |  |  |  |  | CP | DIS. CAPACITY |  |  |  | MAX. |  | 100 | ㎖/min
8 | SPECIFIC GR. | [5 empty] | DIS. PRESS |  |  |  | MAX. |  | 10 | kgf/㎠
9 | CAPACITY |  |  |  |  | ㎖/min | RELIEF V/V SET. PRESS. | [5 empty] | 13 | kgf/㎠
10 | DIS. PRESS |  |  |  |  | kgf/㎠G | STROKE SPEED | [5 empty] | 116 | S.P.M
11 | SUC. PRESS |  |  |  |  | kgf/㎠G | PISTON DIAMETER | [5 empty] | 12 | mm
12 | NPSHa |  |  |  |  | M | STROKE LENGTH | [5 empty] | 10 | mm
13 | INSTALLATION | [5 empty] | NPSHr | [5 empty] | 2 | M
14 | CONSTRUCTION | [5 empty] | INSTALLATION |  |  | INDOOR
15 | DIAPHRAGM TYPE | HYDRAULIC |  |  |  |  | LIQUID END MATERIAL
16 | HEAD NUMBER | SINGLE |  |  |  |  | PUMP HEAD |  |  | PVC
17 | RELIEF VALVE | INTERNAL |  |  |  |  | DIAPHRAGM |  |  | PTFE + PFA
18 | MOTOR MOUNT | HORIZONTAL |  |  |  |  | CHECK BALL |  |  | CERAMIC
19 | CONNECTION TYPE | FLANGE |  |  |  |  | BALL GUIDE |  |  | GFPP
20 | SUC. SIZE | KS 10K 15A RF / LAP JOINT |  |  |  |  | BALL SEAT |  |  | SANTOPRENE
21 | DIS. SIZE | KS 10K 15A RF / LAP JOINT |  |  |  |  | JOINT |  |  | PVC
22 | CAPACITY CONTROL | [5 empty] | O-RING |  |  | SANTOPRENE
23 | TYPE | MANUAL |  |  |  |  | AC INDUCTION MOTOR SPEC.
24 | METHOD | STROKE ADJUSTMENT |  |  |  |  | MAKER |  |  | SHINKANG ELEC.
25 | FLOW RANGE | 10 TO 100% RATED |  |  |  |  | ENCLOSURE |  |  | TEFC
26 | PAINTING COLOR (Munsell No.) | [5 empty] | RATED OUTPUT |  |  | 0.2
27 | GEAR BOX, BED | 0.6PB 4.8/10.6 |  |  |  |  | VOLTAGE/PHASE/CYCLE |  |  | 220,380V / 3Φ/ 60HZ
28 | MOTOR | 6.3G 8.2/0.4 |  |  |  |  | POLE / SPEED |  |  | 4P / 1700RPM
29 | [6 empty] | INSULATION CLASS |  |  | B
30 | APPROX. WEIGHT |  | 20 | KG |  |  | PROTECTION DEGREE |  |  | IP44
31 | [6 empty] | HUB SIZE |  |  | 21
32 | ACCESSORIES | [5 empty] | SPARE PARTS
33 | NAME | SPEC. |  |  |  | Q'TY | NAME |  |  | SPEC. |  |  |  | Q'TY
34
35
36
37
38 | REMARKS : | [5 empty] | REV. | PREPD BY | CHKD BY |  |  |  | APPRVD BY
39 | [6 empty] | 0 | H. R. CHA
41
| 양식 S-01-01 |  |  |  | CHEON SEI IND. CO., LTD. | [6 empty] | A4 (210×297)

## FTC
| 천 세 산 업 주 식 회 사 CHEON SEI IND. CO., LTD. | [5 empty] | METERING PUMP
DATA SHEET
1 | PURCHASER | [5 empty] | ITEM NO.
2 | PROJECT | [5 empty] | SERVICE
3 | JOB NO. | [5 empty] | QUANTITY |  |  |  | SET
4 | OPERATION CONDITIONS | [5 empty] | PUMP SPECIFICATION
5 | LIQUID NAME | [5 empty] | MODEL |  |  | KHV1-12S-FTC-FS
6 | PUMPING TEMP. |  |  |  |  | ℃ | PUMPING TEMP. |  |  | AMB
7 | VISCOSITY |  |  |  |  | CP | DIS. CAPACITY |  |  |  | MAX. |  | 100 | ㎖/min
8 | SPECIFIC GR. | [5 empty] | DIS. PRESS |  |  |  | MAX. |  | 10 | kgf/㎠
9 | CAPACITY |  |  |  |  | ㎖/min | RELIEF V/V SET. PRESS. | [5 empty] | 13 | kgf/㎠
10 | DIS. PRESS |  |  |  |  | kgf/㎠G | STROKE SPEED | [5 empty] | 116 | S.P.M
11 | SUC. PRESS |  |  |  |  | kgf/㎠G | PISTON DIAMETER | [5 empty] | 12 | mm
12 | NPSHa |  |  |  |  | M | STROKE LENGTH | [5 empty] | 10 | mm
13 | INSTALLATION | [5 empty] | NPSHr | [5 empty] | 2 | M
14 | CONSTRUCTION | [5 empty] | INSTALLATION |  |  | INDOOR
15 | DIAPHRAGM TYPE | HYDRAULIC |  |  |  |  | LIQUID END MATERIAL
16 | HEAD NUMBER | SINGLE |  |  |  |  | PUMP HEAD |  |  | PVDF
17 | RELIEF VALVE | INTERNAL |  |  |  |  | DIAPHRAGM |  |  | PTFE + PFA
18 | MOTOR MOUNT | VERTICAL |  |  |  |  | CHECK BALL |  |  | CERAMIC
19 | CONNECTION TYPE | FLANGE |  |  |  |  | BALL GUIDE |  |  | PVDF
20 | SUC. SIZE | KS 10K 15A RF / LAP JOINT |  |  |  |  | BALL SEAT |  |  | SANTOPRENE
21 | DIS. SIZE | KS 10K 15A RF / LAP JOINT |  |  |  |  | JOINT |  |  | PVDF
22 | CAPACITY CONTROL | [5 empty] | O-RING |  |  | SANTOPRENE
23 | TYPE | MANUAL |  |  |  |  | AC INDUCTION MOTOR SPEC.
24 | METHOD | STROKE ADJUSTMENT |  |  |  |  | MAKER |  |  | SHINKANG ELEC.
25 | FLOW RANGE | 10 TO 100% RATED |  |  |  |  | ENCLOSURE |  |  | TEFC
26 | PAINTING COLOR (Munsell No.) | [5 empty] | RATED OUTPUT |  |  | 0.2
27 | GEAR BOX, BED | 0.6PB 4.8/10.6 |  |  |  |  | VOLTAGE/PHASE/CYCLE |  |  | 220,380V / 3Φ/ 60HZ
28 | MOTOR | 0.6PB 4.8/10.6 |  |  |  |  | POLE / SPEED |  |  | 4P / 1700RPM
29 | [6 empty] | INSULATION CLASS |  |  | B
30 | APPROX. WEIGHT |  | 17.5 | KG |  |  | PROTECTION DEGREE |  |  | IP44
31 | [6 empty] | HUB SIZE |  |  | 21
32 | ACCESSORIES | [5 empty] | SPARE PARTS
33 | NAME | SPEC. |  |  |  | Q'TY | NAME |  |  | SPEC. |  |  |  | Q'TY
34
35
36
37
38 | REMARKS : | [5 empty] | REV. | PREPD BY | CHKD BY |  |  |  | APPRVD BY
39 | [6 empty] | 0 | H. R. CHA
41
| 양식 S-01-01 |  |  |  | CHEON SEI IND. CO., LTD. | [6 empty] | A4 (210×297)
| 천 세 산 업 주 식 회 사 CHEON SEI IND. CO., LTD. | [5 empty] | METERING PUMP
DATA SHEET
1 | PURCHASER | [5 empty] | ITEM NO.
2 | PROJECT | [5 empty] | SERVICE
3 | JOB NO. | [5 empty] | QUANTITY |  |  |  | SET
4 | OPERATION CONDITIONS | [5 empty] | PUMP SPECIFICATION
5 | LIQUID NAME | [5 empty] | MODEL |  |  | KHH1-12S-FTC-FS
6 | PUMPING TEMP. |  |  |  |  | ℃ | PUMPING TEMP. |  |  | AMB
7 | VISCOSITY |  |  |  |  | CP | DIS. CAPACITY |  |  |  | MAX. |  | 100 | ㎖/min
8 | SPECIFIC GR. | [5 empty] | DIS. PRESS |  |  |  | MAX. |  | 10 | kgf/㎠
9 | CAPACITY |  |  |  |  | ㎖/min | RELIEF V/V SET. PRESS. | [5 empty] | 13 | kgf/㎠
10 | DIS. PRESS |  |  |  |  | kgf/㎠G | STROKE SPEED | [5 empty] | 116 | S.P.M
11 | SUC. PRESS |  |  |  |  | kgf/㎠G | PISTON DIAMETER | [5 empty] | 12 | mm
12 | NPSHa |  |  |  |  | M | STROKE LENGTH | [5 empty] | 10 | mm
13 | INSTALLATION | [5 empty] | NPSHr | [5 empty] | 2 | M
14 | CONSTRUCTION | [5 empty] | INSTALLATION |  |  | INDOOR
15 | DIAPHRAGM TYPE | HYDRAULIC |  |  |  |  | LIQUID END MATERIAL
16 | HEAD NUMBER | SINGLE |  |  |  |  | PUMP HEAD |  |  | PVDF
17 | RELIEF VALVE | INTERNAL |  |  |  |  | DIAPHRAGM |  |  | PTFE + PFA
18 | MOTOR MOUNT | HORIZONTAL |  |  |  |  | CHECK BALL |  |  | CERAMIC
19 | CONNECTION TYPE | FLANGE |  |  |  |  | BALL GUIDE |  |  | PVDF
20 | SUC. SIZE | KS 10K 15A RF / LAP JOINT |  |  |  |  | BALL SEAT |  |  | SANTOPRENE
21 | DIS. SIZE | KS 10K 15A RF / LAP JOINT |  |  |  |  | JOINT |  |  | PVDF
22 | CAPACITY CONTROL | [5 empty] | O-RING |  |  | SANTOPRENE
23 | TYPE | MANUAL |  |  |  |  | AC INDUCTION MOTOR SPEC.
24 | METHOD | STROKE ADJUSTMENT |  |  |  |  | MAKER |  |  | SHINKANG ELEC.
25 | FLOW RANGE | 10 TO 100% RATED |  |  |  |  | ENCLOSURE |  |  | TEFC
26 | PAINTING COLOR (Munsell No.) | [5 empty] | RATED OUTPUT |  |  | 0.2
27 | GEAR BOX, BED | 0.6PB 4.8/10.6 |  |  |  |  | VOLTAGE/PHASE/CYCLE |  |  | 220,380V / 3Φ/ 60HZ
28 | MOTOR | 6.3G 8.2/0.4 |  |  |  |  | POLE / SPEED |  |  | 4P / 1700RPM
29 | [6 empty] | INSULATION CLASS |  |  | B
30 | APPROX. WEIGHT |  | 20 | KG |  |  | PROTECTION DEGREE |  |  | IP44
31 | [6 empty] | HUB SIZE |  |  | 21
32 | ACCESSORIES | [5 empty] | SPARE PARTS
33 | NAME | SPEC. |  |  |  | Q'TY | NAME |  |  | SPEC. |  |  |  | Q'TY
34
35
36
37
38 | REMARKS : | [5 empty] | REV. | PREPD BY | CHKD BY |  |  |  | APPRVD BY
39 | [6 empty] | 0 | H. R. CHA
41
| 양식 S-01-01 |  |  |  | CHEON SEI IND. CO., LTD. | [6 empty] | A4 (210×297)

## STS
| 천 세 산 업 주 식 회 사 CHEON SEI IND. CO., LTD. | [5 empty] | METERING PUMP
DATA SHEET
1 | PURCHASER | [5 empty] | ITEM NO.
2 | PROJECT | [5 empty] | SERVICE
3 | JOB NO. | [5 empty] | QUANTITY |  |  |  | SET
4 | OPERATION CONDITIONS | [5 empty] | PUMP SPECIFICATION
5 | LIQUID NAME | [5 empty] | MODEL |  |  | KHV1-12S-STS-FS
6 | PUMPING TEMP. |  |  |  |  | ℃ | PUMPING TEMP. |  |  | AMB
7 | VISCOSITY |  |  |  |  | CP | DIS. CAPACITY |  |  |  | MAX. |  | 100 | ㎖/min
8 | SPECIFIC GR. | [5 empty] | DIS. PRESS |  |  |  | MAX. |  | 30 | kgf/㎠
9 | CAPACITY |  |  |  |  | ㎖/min | RELIEF V/V SET. PRESS. | [5 empty] | 36 | kgf/㎠
10 | DIS. PRESS |  |  |  |  | kgf/㎠G | STROKE SPEED | [5 empty] | 116 | S.P.M
11 | SUC. PRESS |  |  |  |  | kgf/㎠G | PISTON DIAMETER | [5 empty] | 12 | mm
12 | NPSHa |  |  |  |  | M | STROKE LENGTH | [5 empty] | 10 | mm
13 | INSTALLATION | [5 empty] | NPSHr | [5 empty] | 2 | M
14 | CONSTRUCTION | [5 empty] | INSTALLATION |  |  | INDOOR
15 | DIAPHRAGM TYPE | HYDRAULIC |  |  |  |  | LIQUID END MATERIAL
16 | HEAD NUMBER | SINGLE |  |  |  |  | PUMP HEAD |  |  | STS304
17 | RELIEF VALVE | INTERNAL |  |  |  |  | DIAPHRAGM |  |  | PTFE + PFA
18 | MOTOR MOUNT | VERTICAL |  |  |  |  | CHECK BALL |  |  | STS304
19 | CONNECTION TYPE | FLANGE |  |  |  |  | BALL GUIDE |  |  | STS304
20 | SUC. SIZE | KS20K 15A FF |  |  |  |  | BALL SEAT |  |  | STS304
21 | DIS. SIZE | KS20K 15A FF |  |  |  |  | JOINT(FLANGE) |  |  | STS304 + SSC13
22 | CAPACITY CONTROL | [5 empty] | GASKET |  |  | PTFE + PFA
23 | TYPE | MANUAL |  |  |  |  | AC INDUCTION MOTOR SPEC.
24 | METHOD | STROKE ADJUSTMENT |  |  |  |  | MAKER |  |  | SHINKANG ELEC.
25 | FLOW RANGE | 10 TO 100% RATED |  |  |  |  | ENCLOSURE |  |  | TEFC
26 | PAINTING COLOR (Munsell No.) | [5 empty] | RATED OUTPUT |  |  | 0.2
27 | GEAR BOX, BED | 0.6PB 4.8/10.6 |  |  |  |  | VOLTAGE/PHASE/CYCLE |  |  | 220,380V / 3Φ/ 60HZ
28 | MOTOR | 0.6PB 4.8/10.6 |  |  |  |  | POLE / SPEED |  |  | 4P / 1700RPM
29 | [6 empty] | INSULATION CLASS |  |  | B
30 | APPROX. WEIGHT |  | 19.5 | KG |  |  | PROTECTION DEGREE |  |  | IP44
31 | [6 empty] | HUB SIZE |  |  | 21
32 | ACCESSORIES | [5 empty] | SPARE PARTS
33 | NAME | SPEC. |  |  |  | Q'TY | NAME |  |  | SPEC. |  |  |  | Q'TY
34
35
36
37
38 | REMARKS : | [5 empty] | REV. | PREPD BY | CHKD BY |  |  |  | APPRVD BY
39 | [6 empty] | 0 | H. R. CHA
41
| 양식 S-01-01 |  |  |  | CHEON SEI IND. CO., LTD. | [6 empty] | A4 (210×297)
| 천 세 산 업 주 식 회 사 CHEON SEI IND. CO., LTD. | [5 empty] | METERING PUMP
DATA SHEET
1 | PURCHASER | [5 empty] | ITEM NO.
2 | PROJECT | [5 empty] | SERVICE
3 | JOB NO. | [5 empty] | QUANTITY |  |  |  | SET
4 | OPERATION CONDITIONS | [5 empty] | PUMP SPECIFICATION
5 | LIQUID NAME | [5 empty] | MODEL |  |  | KHH1-12S-STS-FS
6 | PUMPING TEMP. |  |  |  |  | ℃ | PUMPING TEMP. |  |  | AMB
7 | VISCOSITY |  |  |  |  | CP | DIS. CAPACITY |  |  |  | MAX. |  | 100 | ㎖/min
8 | SPECIFIC GR. | [5 empty] | DIS. PRESS |  |  |  | MAX. |  | 30 | kgf/㎠
9 | CAPACITY |  |  |  |  | ㎖/min | RELIEF V/V SET. PRESS. | [5 empty] | 36 | kgf/㎠
10 | DIS. PRESS |  |  |  |  | kgf/㎠G | STROKE SPEED | [5 empty] | 116 | S.P.M
11 | SUC. PRESS |  |  |  |  | kgf/㎠G | PISTON DIAMETER | [5 empty] | 12 | mm
12 | NPSHa |  |  |  |  | M | STROKE LENGTH | [5 empty] | 10 | mm
13 | INSTALLATION | [5 empty] | NPSHr | [5 empty] | 2 | M
14 | CONSTRUCTION | [5 empty] | INSTALLATION |  |  | INDOOR
15 | DIAPHRAGM TYPE | HYDRAULIC |  |  |  |  | LIQUID END MATERIAL
16 | HEAD NUMBER | SINGLE |  |  |  |  | PUMP HEAD |  |  | STS304
17 | RELIEF VALVE | INTERNAL |  |  |  |  | DIAPHRAGM |  |  | PTFE + PFA
18 | MOTOR MOUNT | HORIZONTAL |  |  |  |  | CHECK BALL |  |  | STS316
19 | CONNECTION TYPE | FLANGE |  |  |  |  | BALL GUIDE |  |  | STS304
20 | SUC. SIZE | KS20K 15A FF |  |  |  |  | BALL SEAT |  |  | STS304
21 | DIS. SIZE | KS20K 15A FF |  |  |  |  | JOINT(FLANGE) |  |  | STS304 + SSC13
22 | CAPACITY CONTROL | [5 empty] | GASKET |  |  | PTFE + PFA
23 | TYPE | MANUAL |  |  |  |  | AC INDUCTION MOTOR SPEC.
24 | METHOD | STROKE ADJUSTMENT |  |  |  |  | MAKER |  |  | SHINKANG ELEC.
25 | FLOW RANGE | 10 TO 100% RATED |  |  |  |  | ENCLOSURE |  |  | TEFC
26 | PAINTING COLOR (Munsell No.) | [5 empty] | RATED OUTPUT |  |  | 0.2
27 | GEAR BOX, BED | 0.6PB 4.8/10.6 |  |  |  |  | VOLTAGE/PHASE/CYCLE |  |  | 220,380V / 3Φ/ 60HZ
28 | MOTOR | 6.3G 8.2/0.4 |  |  |  |  | POLE / SPEED |  |  | 4P / 1700RPM
29 | [6 empty] | INSULATION CLASS |  |  | B
30 | APPROX. WEIGHT |  | 22 | KG |  |  | PROTECTION DEGREE |  |  | IP44
31 | [6 empty] | HUB SIZE |  |  | 21
32 | ACCESSORIES | [5 empty] | SPARE PARTS
33 | NAME | SPEC. |  |  |  | Q'TY | NAME |  |  | SPEC. |  |  |  | Q'TY
34
35
36
37
38 | REMARKS : | [5 empty] | REV. | PREPD BY | CHKD BY |  |  |  | APPRVD BY
39 | [6 empty] | 0 | H. R. CHA
41
| 양식 S-01-01 |  |  |  | CHEON SEI IND. CO., LTD. | [6 empty] | A4 (210×297)

## 6T6
| 천 세 산 업 주 식 회 사 CHEON SEI IND. CO., LTD. | [5 empty] | METERING PUMP
DATA SHEET
1 | PURCHASER | [5 empty] | ITEM NO.
2 | PROJECT | [5 empty] | SERVICE
3 | JOB NO. | [5 empty] | QUANTITY |  |  |  | SET
4 | OPERATION CONDITIONS | [5 empty] | PUMP SPECIFICATION
5 | LIQUID NAME | [5 empty] | MODEL |  |  | KHV1-12S-6T6-FS
6 | PUMPING TEMP. |  |  |  |  | ℃ | PUMPING TEMP. |  |  | AMB
7 | VISCOSITY |  |  |  |  | CP | DIS. CAPACITY |  |  |  | MAX. |  | 100 | ㎖/min
8 | SPECIFIC GR. | [5 empty] | DIS. PRESS |  |  |  | MAX. |  | 30 | kgf/㎠
9 | CAPACITY |  |  |  |  | ㎖/min | RELIEF V/V SET. PRESS. | [5 empty] | 36 | kgf/㎠
10 | DIS. PRESS |  |  |  |  | kgf/㎠G | STROKE SPEED | [5 empty] | 116 | S.P.M
11 | SUC. PRESS |  |  |  |  | kgf/㎠G | PISTON DIAMETER | [5 empty] | 12 | mm
12 | NPSHa |  |  |  |  | M | STROKE LENGTH | [5 empty] | 10 | mm
13 | INSTALLATION | [5 empty] | NPSHr | [5 empty] | 2 | M
14 | CONSTRUCTION | [5 empty] | INSTALLATION |  |  | INDOOR
15 | DIAPHRAGM TYPE | HYDRAULIC |  |  |  |  | LIQUID END MATERIAL
16 | HEAD NUMBER | SINGLE |  |  |  |  | PUMP HEAD |  |  | STS316
17 | RELIEF VALVE | INTERNAL |  |  |  |  | DIAPHRAGM |  |  | PTFE + PFA
18 | MOTOR MOUNT | VERTICAL |  |  |  |  | CHECK BALL |  |  | STS316
19 | CONNECTION TYPE | FLANGE |  |  |  |  | BALL GUIDE |  |  | STS316
20 | SUC. SIZE | KS20K 15A FF |  |  |  |  | BALL SEAT |  |  | STS316
21 | DIS. SIZE | KS20K 15A FF |  |  |  |  | JOINT(FLANGE) |  |  | STS316 + SSC14
22 | CAPACITY CONTROL | [5 empty] | GASKET |  |  | PTFE + PFA
23 | TYPE | MANUAL |  |  |  |  | AC INDUCTION MOTOR SPEC.
24 | METHOD | STROKE ADJUSTMENT |  |  |  |  | MAKER |  |  | SHINKANG ELEC.
25 | FLOW RANGE | 10 TO 100% RATED |  |  |  |  | ENCLOSURE |  |  | TEFC
26 | PAINTING COLOR (Munsell No.) | [5 empty] | RATED OUTPUT |  |  | 0.2
27 | GEAR BOX, BED | 0.6PB 4.8/10.6 |  |  |  |  | VOLTAGE/PHASE/CYCLE |  |  | 220,380V / 3Φ/ 60HZ
28 | MOTOR | 0.6PB 4.8/10.6 |  |  |  |  | POLE / SPEED |  |  | 4P / 1700RPM
29 | [6 empty] | INSULATION CLASS |  |  | B
30 | APPROX. WEIGHT |  | 19.5 | KG |  |  | PROTECTION DEGREE |  |  | IP44
31 | [6 empty] | HUB SIZE |  |  | 21
32 | ACCESSORIES | [5 empty] | SPARE PARTS
33 | NAME | SPEC. |  |  |  | Q'TY | NAME |  |  | SPEC. |  |  |  | Q'TY
34
35
36
37
38 | REMARKS : | [5 empty] | REV. | PREPD BY | CHKD BY |  |  |  | APPRVD BY
39 | [6 empty] | 0 | H. R. CHA
41
| 양식 S-01-01 |  |  |  | CHEON SEI IND. CO., LTD. | [6 empty] | A4 (210×297)
| 천 세 산 업 주 식 회 사 CHEON SEI IND. CO., LTD. | [5 empty] | METERING PUMP
DATA SHEET
1 | PURCHASER | [5 empty] | ITEM NO.
2 | PROJECT | [5 empty] | SERVICE
3 | JOB NO. | [5 empty] | QUANTITY |  |  |  | SET
4 | OPERATION CONDITIONS | [5 empty] | PUMP SPECIFICATION
5 | LIQUID NAME | [5 empty] | MODEL |  |  | KHH1-12S-6T6-FS
6 | PUMPING TEMP. |  |  |  |  | ℃ | PUMPING TEMP. |  |  | AMB
7 | VISCOSITY |  |  |  |  | CP | DIS. CAPACITY |  |  |  | MAX. |  | 100 | ㎖/min
8 | SPECIFIC GR. | [5 empty] | DIS. PRESS |  |  |  | MAX. |  | 30 | kgf/㎠
9 | CAPACITY |  |  |  |  | ㎖/min | RELIEF V/V SET. PRESS. | [5 empty] | 36 | kgf/㎠
10 | DIS. PRESS |  |  |  |  | kgf/㎠G | STROKE SPEED | [5 empty] | 116 | S.P.M
11 | SUC. PRESS |  |  |  |  | kgf/㎠G | PISTON DIAMETER | [5 empty] | 12 | mm
12 | NPSHa |  |  |  |  | M | STROKE LENGTH | [5 empty] | 10 | mm
13 | INSTALLATION | [5 empty] | NPSHr | [5 empty] | 2 | M
14 | CONSTRUCTION | [5 empty] | INSTALLATION |  |  | INDOOR
15 | DIAPHRAGM TYPE | HYDRAULIC |  |  |  |  | LIQUID END MATERIAL
16 | HEAD NUMBER | SINGLE |  |  |  |  | PUMP HEAD |  |  | STS316
17 | RELIEF VALVE | INTERNAL |  |  |  |  | DIAPHRAGM |  |  | PTFE + PFA
18 | MOTOR MOUNT | HORIZONTAL |  |  |  |  | CHECK BALL |  |  | STS316
19 | CONNECTION TYPE | FLANGE |  |  |  |  | BALL GUIDE |  |  | STS316
20 | SUC. SIZE | KS20K 15A FF |  |  |  |  | BALL SEAT |  |  | STS316
21 | DIS. SIZE | KS20K 15A FF |  |  |  |  | JOINT(FLANGE) |  |  | STS316 + SSC14
22 | CAPACITY CONTROL | [5 empty] | GASKET |  |  | PTFE + PFA
23 | TYPE | MANUAL |  |  |  |  | AC INDUCTION MOTOR SPEC.
24 | METHOD | STROKE ADJUSTMENT |  |  |  |  | MAKER |  |  | SHINKANG ELEC.
25 | FLOW RANGE | 10 TO 100% RATED |  |  |  |  | ENCLOSURE |  |  | TEFC
26 | PAINTING COLOR (Munsell No.) | [5 empty] | RATED OUTPUT |  |  | 0.2
27 | GEAR BOX, BED | 0.6PB 4.8/10.6 |  |  |  |  | VOLTAGE/PHASE/CYCLE |  |  | 220,380V / 3Φ/ 60HZ
28 | MOTOR | 6.3G 8.2/0.4 |  |  |  |  | POLE / SPEED |  |  | 4P / 1700RPM
29 | [6 empty] | INSULATION CLASS |  |  | B
30 | APPROX. WEIGHT |  | 22 | KG |  |  | PROTECTION DEGREE |  |  | IP44
31 | [6 empty] | HUB SIZE |  |  | 21
32 | ACCESSORIES | [5 empty] | SPARE PARTS
33 | NAME | SPEC. |  |  |  | Q'TY | NAME |  |  | SPEC. |  |  |  | Q'TY
34
35
36
37
38 | REMARKS : | [5 empty] | REV. | PREPD BY | CHKD BY |  |  |  | APPRVD BY
39 | [6 empty] | 0 | H. R. CHA
41
| 양식 S-01-01 |  |  |  | CHEON SEI IND. CO., LTD. | [6 empty] | A4 (210×297)